Declaration of Performance

No. 027-DOP-2024-10-28

| 1. | Unique identification code of the product-type: | Multi-wall Metal System Chimney (with 25 and 50 mm insulation) ICS 5000 |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 2. | Intended use: | Convey the products of combustion from heating appliances to the outside atmosphere |  |  |  |  |
| 3. | Product designations: |  | Model 1 | DN (80 – 300) |  | T600 H1 D V3 L50050 O75 |
|  |  |  |  | DN (350 - 450) |  | T600 H1 D V3 L50050 O112,5 |
|  |  |  |  | DN (500 - 600) |  | T600 H1 D V3 L50050 O150 |
|  |  |  | Model 2 | DN (80 – 300) |  | T600 H1 D V2 L99050 O75 |
|  |  |  |  | DN (350 - 450) |  | T600 H1 D V2 L99050 O112,5 |
|  |  |  |  | DN (500 - 600) |  | T600 H1 D V2 L99050 O150 |
|  |  |  | Model 3 | DN (80 – 300) |  | T600 H1 D Vm L20050 O75 |
|  |  |  |  | DN (350 - 450) |  | T600 H1 D Vm L20050 O112,5 |
|  |  |  |  | DN (500 - 600) |  | T600 H1 D Vm L20050 O150 |
|  |  |  | Model 4 | DN (80 – 200) |  | T200 H1 W V2 L50050 O50 |
|  |  |  | Model 5 | DN (80 – 300) |  | T600 H1 D V3 L50050 O25 |
|  |  |  |  | DN (350 - 450) |  | T600 H1 D V3 L50050 O37,5 |
|  |  |  |  | DN (500 - 600) |  | T600 H1 D V3 L50050 O50 |
|  |  |  | Model 6 | DN (80 – 300) |  | T600 H1 D V2 L99050 O25 |
|  |  |  |  | DN (350 - 450) |  | T600 H1 D V2 L99050 O37,5 |
|  |  |  |  | DN (500 - 600) |  | T600 H1 D V2 L99050 O50 |
|  |  |  | Model 7 | DN (80 – 300) |  | T600 H1 D Vm L20050 O25 |
|  |  |  |  | DN (350 - 450) |  | T600 H1 D Vm L20050 O37,5 |
|  |  |  |  | DN (500 - 600) |  | T600 H1 D Vm L20050 O50 |
|  |  |  | L99 material = 1.4521 (444) |  |  |  |
|  |  | Models 1 - 4 with 25 mm insulation Models 5 - 7 with 50 mm insulation |  |  |  |  |
| 4. | Manufacturer: | Schiedel Chimney systems Ltd., Crowther Estate, Washington, Tyne & Wear NE38 0AQ, Great Britain |  |  |  |  |
| 5. | Authorized representative: | N/A |  |  |  |  |
| 6. | System(s) of AVCP: | System 2+ (and System 4 for terminals) |  |  |  |  |
| 7. | Harmonized standard: | EN 1856-1:2009 |  |  |  |  |
|  | Notified body: | 0036 |  |  |  |  |

8.	Declared performance:

| Essential characteristics | Performance | Harmonized technical specification |
| --- | --- | --- |
| Compressive strength | Model(s) 1 to 4: DN (80 – 130): 22 m DN (150 - 180): 18 m DN (200 - 300): 18 m DN (350 - 450): 12 m DN (500 - 550): 12 m DN (600): 10 m Model(s) 5 to 7: DN (80 - 300): 15 m DN (350 - 600): 10 m | EN 1856-1: 2009 |
| Chimney sections, fittings and supports | For further information see installation instructions |  |
| Resistance to fire | Model(s) 1 to 3: DN (80 – 300): T600 O75 DN (350 - 450): T600 O112,5 DN (500 - 600): T600 O150 Model 4: DN (80 – 200): T200 O50 Model(s) 5 to 7: DN (80 – 300): T600 O25 DN (350 - 450): T600 O37,5 DN (500 - 600): T600 O50 Tested fully ventilated | EN 1856-1: 2009 |
| Gas tightness /leakage | Model(s) 1 to 7: DN (80 – 600): H1 | EN 1856-1: 2009 |
| Flow resistance of chimney sections | Model(s) 1 to 7: DN (80 – 600): 1,0 mm | EN 1856-1: 2009 |
| Flow resistance of chimney fittings Flow resistance of terminals | Zeta 0.3 according EN 13384-1 Zeta 0.5 according EN 13384-1 |  |
| Thermal resistance | Model(s) 1 to 4: DN (80 – 600): 0.37 m2 K/W tested at 200°C Model(s) 5 & 7: DN (80 – 600): 0.56 m2 K/W tested at 200°C | EN 1856-1: 2009 |
| Thermal shock resistance Sootfire resistance: | Model(s) 1 to 7: DN (80 – 600): No | EN 1856-1: 2009 |
| Thermal performance under normal operating conditions: | Model(s) 1, 2, 3, 5, 6, 7: DN (80 – 600): T600 Model 4: DN (80 – 200): T200 |  |

| Essential characteristics | Performance | Harmonized technical specification |
| --- | --- | --- |
| Flexural tensile strength (only for means of connection for chimney sections and fittings) | Model(s) 1 to 4: DN 80 = 48 metres DN 200 = 21 metres DN 300 = 15 metres DN 600 = 6 metres Model(s) 5 & 7: DN 100 = 25 metres DN 300 = 11 metres DN 600 = 6 metres | EN 1856-1: 2009 |
| Non-vertical installation | Model(s) 1 to 4: DN (80 – 500): between supports ≤ 3 m at 90° DN (550 - 600): between supports ≤ 4 m at 90° Model(s) 5 & 7: DN (80 – 500): between supports ≤ 3 m at 90° DN (550 - 600): between supports ≤ 4 m at 90° | EN 1856-1: 2009 |
| Components subject to wind load | Model(s) 1 to 7: DN (80 – 400): ≤ 3 m above last support ≤ 4 m between supports DN (450 - 600): ≤ 2 m above last support ≤ 3 m between supports | EN 1856-1: 2009 |
| Durability |  | EN 1856-1: 2009 |
| Water and vapour diffusion resistance | Model(s) 1, 2, 3, 5, 6, 7: DN (80 – 600): No Model 4: DN (80 – 200): Yes |  |
| Condensate penetration resistance | Model(s) 1, 2, 3, 5, 6, 7: DN (80 – 600): No Model 4: DN (80 – 200): Yes |  |
| Durability against corrosion | Model(s) 1 & 5: DN (80 – 600): V3 Model(s) 2, 4 & 6: DN (80 – 600): V2 Model(s) 3 & 7: DN (80 – 600): Vm |  |
| Freeze-thaw resistance | Model(s) 1 to 7: DN (80 – 600): Yes |  |

The performance of the product identified above is in conformity with the set of declared performance/s. This declaration of performance is issued in accordance with Regulation (EU) No 305/2011, under the sole responsibility of the manufacturer identified above.

Washington, 28.10.2024						Michael Ball,

Chief Executive Officer