- Declaration of Performance

No. 038-DOP-2024-10-28

| 1. | Unique identification code of the product type: |  | Double-wall connecting flue pipe (with 25 and 50 mm insulation) ICS 5000 |  |  |
| --- | --- | --- | --- | --- | --- |
| 2. | Intended use: |  | Convey the products of combustion from heating appliances to the chimney |  |  |
| 3. | Product designations: | Model 1 |  | DN (80 – 300) | T600 H1 D V3 – L50050 O100 M |
|  |  |  |  | DN (350 – 450) | T600 H1 D V3 – L50050 O150 M |
|  |  |  |  | DN (500 – 600) | T600 H1 D V3 – L50050 O200 M |
|  |  | Model 2* |  | DN (80 – 300) | T600 H1 D V2 – L99050 O100 M |
|  |  |  |  | DN (350 – 450) | T600 H1 D V2 – L99050 O150 M |
|  |  |  |  | DN (500 – 600) | T600 H1 D V2 – L99050 O200 M |
|  |  | Model 3 |  | DN (80 – 300) | T600 H1 D Vm – L20050 O100 M |
|  |  |  |  | DN (350 – 450) | T600 H1 D Vm – L20050 O150 M |
|  |  |  |  | DN (500 – 600) | T600 H1 D Vm – L20050 O200 M |
|  |  |  | *L99 material = 1.4521 (444) Models valid for both 25 and 50 mm insulation |  |  |
| 4. | Manufacturer: |  | Schiedel Chimney systems Ltd., Crowther Estate, Washington, Tyne & Wear NE38 0AQ, Great Britain |  |  |
| 5. | Authorized representative: |  | N/A |  |  |
| 6. | System(s) of AVCP: |  | System 2+ |  |  |
| 7. | Harmonized standard: |  | EN 1856-2:2009 |  |  |
|  | Notified body: |  | 0036 |  |  |

8.	Declared performance:

| Essential characteristics | Performance | Harmonized technical specification |
| --- | --- | --- |
| Compressive strength | Model(s) 1 to 3 (with 25 mm of insulation): DN (80 – 130): 22 m DN (150 - 300): 18 m DN (350 - 550): 12 m DN (600): 10 m Model(s) 1 to 3 (with 50 mm of insulation): DN (80 – 300): 15 m DN (350 – 300): 10 m | EN 1856-2: 2009 |
| Resistance to fire | Model(s) 1 to 3: DN (80 – 300): O100 M DN (350 – 450): O150 M DN (450 – 600): O200 M | EN 1856-2: 2009 |

| Essential characteristics | Performance | Harmonized technical specification |
| --- | --- | --- |
| Gas tightness /leakage | Model(s) 1 to 3: DN (80 – 600): H1 | EN 1856-2: 2009 |
| Flow resistance of chimney sections | Model(s) 1 to 3: DN (80 – 600): 1,0 mm | EN 1856-2: 2009 |
| Flow resistance of chimney fittings | According EN 13384-1 | EN 13384-1: 2014 |
| Thermal resistance | Model(s) 1 to 3 (with 25 mm of insulation): DN (80 – 600): 0.37 m2 K/W tested at 200°C Model(s) 1 to 3 (with 50 mm of insulation): DN (80 – 600): 0.56 m2 K/W tested at 200°C | EN 1856-2: 2009 |
| Thermal shock resistance |  | EN 1856-2: 2009 |
| Sootfire resistance | Model(s) 1 to 3: DN (80 – 600): No |  |
| Thermal performance under normal operating conditions | Model(s) 1 to 3: DN (80 – 600): T600 | EN 1856-2: 2009 |
| Flexural tensile strength | Model(s) 1 to 3: NPD | EN 1856-2: 2009 |
| Non-vertical installation | Model(s) 1 to 3: DN (80 – 500): between supports ≤ 3 m at 90° DN (550 - 600): between supports ≤ 4 m at 90° | EN 1856-2: 2009 |
| Durability |  | EN 1856-2: 2009 |
| Water and vapour diffusion resistance | Model(s) 1 to 3: DN (80 – 600): No |  |
| Condensate penetration resistance | Model(s) 1 to 3: DN (80 – 600): No |  |
| Durability against corrosion | Model(s) 1: DN (80 – 600): V3 Model(s) 2: DN (80 – 600): V2 Model(s) 3: DN (80 – 600): Vm |  |
| Freeze-thaw resistance | Model(s) 1 to 3: DN (80 – 600): Yes |  |

The performance of the product identified above is in conformity with the set of declared performance/s. This declaration of performance is issued in accordance with Regulation (EU) No 305/2011, under the sole responsibility of the manufacturer identified above.

Signed for and on behalf of the manufacturer by:

Washington, 28.10.2024						Michael Ball

Chief Executive Officer